## Sheet1
Technology | Description | Contaminants | Costs | CAPEX | OPEX | Water
Pond System (PS) | Artificial man-made lagoons in which wastewater is treated by natural occurring processes and the influence of solar light, wind, microorganisms and algae. | N: 20–40 \newline P: 60–70 \newline COD: 60–96 \newline SS: 50–90 | CAPEX: $3897.7\cdot x^{-0.407}$ \newline OPEX: $5.543\cdot x + 3127.5$\newline **Energy: $0.19\cdot V$ | \includegraphics[width=3cm]{CAPEX_1} | \includegraphics[width=3cm]{OPEX_1} | Irrigation tailwater
Intermittent Sand Filter (ISF) | Wastewater treated with a well developed aerobic biological community attached to the surface of filter media. | N: 65–95 \newline P: 75–99 \newline COD: 75–90 \newline SS: 85–95 | CAPEX: $2115.5\cdot x^{-0.399}$ \newline OPEX: $12.026\cdot x+3518.9$\newline **Energy: $0.2\cdot V$ | \includegraphics[width=3cm]{CAPEX_2} | \includegraphics[width=3cm]{OPEX_2} | Population wastewater
Wetlands (CWS) | Pretreatment of wastewater by filtration and settling, followed by bacterial decomposition in a natural-looking lined marsh. | N: 30–70 \newline P: 20–60 \newline COD: 55–80 \newline SS: 60–98 | CAPEX: $947.3\cdot x^{-0188}$ \newline OPEX: $14.749\cdot x+3645.1$ \newline **Energy: $0.19\cdot V$ | \includegraphics[width=3cm]{CAPEX_3} | \includegraphics[width=3cm]{OPEX_3} | Irrigation tailwater
Trickling Filter (TF) | A fixed bed over which sewage flows downward developing a layer of microbial slime (biofilm), covering the bed of media. | N: 35–50 \newline P: 35–55 \newline COD: 75–90 \newline SS: 50–90 | CAPEX: $12237\cdot x^{-0.87}$ \newline OPEX: $13.504\cdot x+6020$ \newline **Energy: $0.3\cdot V$ | \includegraphics[width=3cm]{CAPEX_4} | \includegraphics[width=3cm]{OPEX_4} | Population wastewater
Moving Bed Biofilm Reactor (MBBR) | Based on the aerobic biofilm principle. Carriers made from polyethylene provide large surface and optimal conditions for the bacteria culture to develop. | N: 10–20 \newline P: 30–40 \newline COD: 20–40 \newline SS: 60–80 | CAPEX: $1187\cdot x^{-0.165}$ \newline OPEX: $12.794\cdot x+6031$\newline **Energy: $0.8\cdot V$ | \includegraphics[width=3cm]{CAPEX_5} | \includegraphics[width=3cm]{OPEX_5} | Population wastewater
Rotating Biological Contractors (RBC) | Large disk with radial and concentric passages slowly rotating. The alternate exposure to oxygen/sewage promotes the development of a thin layer of biomass. | N: 20–80 \newline P: 10–30 \newline COD: 70–93 \newline SS: 75–98 | CAPEX: $6931.4\cdot x^{-0.383}$ \newline OPEX: $313.4\cdot x^{-0.435}$\newline **Energy: $0.8\cdot V$ | \includegraphics[width=3cm]{CAPEX_6} | \includegraphics[width=3cm]{OPEX_6} | Population wastewater
Membrane Bioreactor (MBR) | Combination of the conventional activated sludge process with a membrane filtration step. | N: 50–90 \newline P: 20–70 \newline COD: 70–90 \newline SS: 85–99 | CAPEX: $5635.3\cdot x^{-0.352}$\newline *OPEX:\newline $2.116\cdot V^{0.713}e^{1.51\cdot SS+0.037\cdot BOD}$\newline **Energy: $0.8\cdot V$ | \includegraphics[width=3cm]{CAPEX_7} | \includegraphics[width=3cm]{OPEX_7} | Population wastewater
Extended Aeration (EA) | Modification of the activated sludge process preferred for small loads, where lower operating efficiency is offset by mechanical simplicity. | N: 50–90 \newline P: 15–70 \newline COD: 70–90 \newline SS: 85–99 | CAPEX: $7946\cdot x^{-0.460}$ \newline *OPEX: $169.48\cdot V^{0.454}e^{0.61\cdot SS}$\newline **Energy: $0.6\cdot V$ | \includegraphics[width=3cm]{CAPEX_8} | \includegraphics[width=3cm]{OPEX_8} | Population wastewater
Sequencing Batch Reactor (SBR) | Fill-and-draw activated sludge system where all the operations (fill, react, settle and draw) are achieved in a single batch reactor. | N: 55–90 \newline P: 25–70 \newline COD: 70–90 \newline SS: 85–99 | CAPEX: $8258.9\cdot x^{-0.407}$ \newline OPEX: $309.4\cdot x^{-0.389}$\newline **Energy: $1\cdot V$ | \includegraphics[width=3cm]{CAPEX_9} | \includegraphics[width=3cm]{OPEX_9} | Population wastewater